## Sheet1
Where the ladder extends over five metres above grade, floor or landing have a safety cage commencing not more than
| a) 2.2 meters above grade | 1
b) 3.3 meters above grade
c) 4.4 meters above grade
d) 5.5 meters above grade
What type of receptacle would you install in a dwelling unit intended to a washing machine?
a) GFCI
| b) Duplex | 1
c) Split
d) Arc-fault
When do you start rough installation in building?
a) After the walls have been erected
b) After the windows and doors are installed
c) After the walls and doors are installed
| d) After the walls and the roof are weather proof | 1
The circuit breakers on a motor control circuit shuts down the motor. What would the electrician check first?
| a) Voltage | 1
b) Current
c) Watts
d) Continuity
The electric hot water heater has power but is not producing hot water. Which tool would you use to test the heater?
a) Ohmmeter
b) Wheatstone Bridge
| c) Clamp on Ammeter | 1
d) Wattmeter
What operation does a "Punch-down Tool" perform?
a) Cut cable only
b) Terminates cable only
c) Strip and terminates cable
| d) Terminates and cuts cable | 1
Three drive belts are connected, one belt from the pulley A to B, one belt from pulley B to C and one belt from pulley C to D. If belt between pulley A and B breaks. Which belt should be replaced?
a] Only the belt from pulley A to B
b) Only the belt from pulley B to C
c) Only the belt from pulley C to D
| d] Replace all the belts | 1
A recently replaced drive belt on a motor pulley is badly worn on one side. What should be done?
a] Replace the worn belt
| b] Replace the belt and align the pulley | 1
c] Replace the belt with the next larger size
d] Replace the motor
A three phase motor is missing one phase. What should the electrician check first?
| a) Overcurrent device | 1
b] Overload device
c] Continuity of windings
d) Bonding connection
An electrician is installing 8 light fixtures in a room 18 meters long. What is the distance from light 1 and light 8 to the closest wall?
a] 2 m
b] 1.5 m
| c) 1.125 m | 1
d) 6 m
To change the angle of a luminaries' light pattern. What you must do?
| a) Change the reflector | 1
b) Change the photo cell
c) Change the light bulb
d) Change the position of the fixture
In a two stage, Class "A" signal circuit. What is indicated by an illuminated light in the panel?
a) System is operational
b) System is in alarm stage
| c) System is in alarm stage, action must be taken within 5 minutes | 1
d} System requires service
"Nurse Emergency Calls Systems" can be re-set at which of the following locations?
| a] Duty Room | 1
b] Central Station
c] Nurse Calls Station
d] Safety Station
What is the smallest integral assembly of four or more conductors that can be used for a "Nurse Call Stations"?
| a] No. 22AWG | 1
b) No. 19AWG
c) No. 16AWG
d] No. 14AWG
What is the minimum 150 amps size of bonding conductor under cellular floors?
a) # 8 AWG
| b) #6 AWG | 1
c) 2/0 AWG
d) 1/0 AWG
What is the maximum ampacity of a # 18 SJOOW cable, with 2 current carrying conductors?
a) 13 amps
b] 7 amps
c] 5 amps
| d) 10 amps | 1
When testing PLC inputs and outputs. What procedure is followed?
| a] Test inputs and outputs individually | 1
b] Test inputs simultaneously
c] Test inputs individually
d] Test outputs individually
What type of conduit can be used in a building constructed of combustible and non-combustible materials?
| a] EMT | 1
b) Electrical non-metallic tubing
c) Rigid PVC conduit
d] Rigid HFT conduit
What type of cable is used for fire alarm systems wiring installed on the outside wall of non-combustible material?
| a) FAS 105, installed in EMT | 1
b) FAS 200
c) ELC
d) FCC
What is the minimum distance a communication cable run in PVC conduit can be installed from a 347 V lighting circuit?
a) 50 mm
b) 150 mm
c) 300 mm
| d) 600 mm | 1
An electrician replaced a 600 V three phase motor in a commercial business, using two way radios. Which of the following statement is correct?
a) One electrician at the start button and the other to check the voltage
| b) One electrician at the start button and the other to check the rotation | 1
c) One electrician at the start button and the other to check the amperage
d) One electrician at the controllers and the other to check the disconnect means
What is the minimum distance a Class 2 cable can be installed from a 120 V power circuit?
| a) 50 mm | 1
b) 250 mm
c) 600 mm
d) 300 mm